## Air Sciences Inc.
Cooling Tower Particulate Air Emissions Calculator
This workbook calculates the particulate (PM) emissions and size fractions (PM10 and PM2.5) from cooling tower water drift. The premise of this calculation is that each water droplet emitted from cooling tower drift loss evaporates, leaving a single particle. The size of that particle is determined by the size of the water droplet, the concentration of the total dissolved solids (TDS) in the droplet, and the density of TDS constituents. Air Sciences Inc. specializes in air pollution compliance, air quality consulting, and environmental consulting. Since 1980, we have worked with industry and government clients. Industry sectors have included minerals extraction and refining, power production, natural gas processing, chemical manufacturing, painting processes, and pesticide formulation. Government work has included fire emissions modeling and fire effects model development for federal land managers, and studies of dust movement, modeling, and mitigation for the EPA. Air Sciences’ in-house services include ambient and meteorological monitoring, regulatory interpretation and application, permitting and compliance, emission inventories, air quality impact assessment, air dispersion and visibility modeling, forest ecology and fire science work, pollution control technology, chemical and process engineering, and data analysis. Our staff of scientists and engineers specialize in air quality, stay informed of changing technologies and regulations, and are committed to customer service while working in the most efficient and cost-effective manner possible.
Need air quality consulting services?
We are here to help!
http://airsci.com/
Denver Office
150 Capital Drive, Suite 320, Golden, CO 80401
303-988-2960
Portland Office
1120 SE Madison St. Portland, OR 97214
503-525-9394

## Cooling Tower Calculator
Cooling Tower Particulate Air Emissions Calculator
COOLING TOWER SPECIFICATIONS:
Enter specifications into blue cells
Drift loss |  |  | 0.0005% |  | High Efficiency
Circulating water flow rate |  |  | 12000 | gpm
Total dissolved solids |  |  | 7000 | ppm
Density of TDS constituents |  |  | 2.5 | g/cc | Average density of common salts (CaCO3, CaSO4, CaCl2, NaCl, Na2SO4, Na2CO3)
Volume of a sphere |  |  | V = 4/3*π*r3
Annual drift |  |  | 29.988 | lb H2O/hr
ANNUAL EMISSIONS:
Total Particulate Emissions |  |  | 0.91089 | ton/yr
PM10 Emissions |  |  | 0.45799 | ton/yr
PM2.5 Emissions |  |  | 0.0018021 | ton/yr
Water Drop Size Distribution for Low Efficiency Drift Eliminators*
Based on a drift rate of 0.001%
Droplet |  |  | H2O Droplet | Solids |  | Emissions
Dia. |  | % mass | Mass | Vol. | Dia. | PM | PM10 | PM2.5
(micron) | % mass | smaller | (g) | (cc) | (micron) | (lb/hr) | (lb/hr) | (lb/hr)
22 | 0.43 | 0.43 | 5.5753e-09 | 1.5611e-11 | 3.1008 |  |  | 0.43%
29 | 1.49 | 1.92 | 1.277e-08 | 3.5756e-11 | 4.0874
44 | 3.76 | 5.68 | 4.4602e-08 | 1.2489e-10 | 6.2016
58 | 2.09 | 7.77 | 1.0216e-07 | 2.8605e-10 | 8.1749
65 | 1.86 | 9.63 | 1.4379e-07 | 4.0262e-10 | 9.1615
87 | 1.56 | 11.19 | 3.4479e-07 | 9.6542e-10 | 12.2623 |  | 11.19%
108 | 1.43 | 12.62 | 6.5958e-07 | 1.8468e-09 | 15.2222
120 | 1.26 | 13.88 | 9.0478e-07 | 2.5334e-09 | 16.9135
132 | 1.09 | 14.97 | 1.2043e-06 | 3.3719e-09 | 18.6049
144 | 1.32 | 16.29 | 1.5635e-06 | 4.3777e-09 | 20.2962
174 | 5.81 | 22.1 | 2.7583e-06 | 7.7233e-09 | 24.5246
300 | 5.04 | 27.14 | 1.4137e-05 | 3.9584e-08 | 42.2838
450 | 4.17 | 31.31 | 4.7713e-05 | 1.336e-07 | 63.4257 | 31.31%
600 | 4.01 | 35.32 | 0.0001131 | 3.1667e-07 | 84.5676
750 | 4 | 39.32 | 0.00022089 | 6.185e-07 | 105.7095
900 | 4.03 | 43.35 | 0.0003817 | 1.0688e-06 | 126.8514
1050 | 4.57 | 47.92 | 0.00060613 | 1.6972e-06 | 147.9933
1200 | 5.46 | 53.38 | 0.00090478 | 2.5334e-06 | 169.1352
1350 | 6.8 | 60.18 | 0.0012882 | 3.6071e-06 | 190.2771
2250 | 17.99 | 78.17 | 0.0059641 | 1.67e-05 | 317.1284
2400 | 21.83 | 100 | 0.0072382 | 2.0267e-05 | 338.2703
* EPA. 1979. Effects of Pathogenic and Toxic Material Transport Via Cooling Device Drift - Vol. 1
Technical Report. EPA-600/7-79-251a. November 1979.
** Maximum droplet size governed by atmospheric dispersion. Larger droplets fall to the ground before
evaporating into a particle (EPA 1979).
Water Drop Size Distribution for High Efficiency Drift Eliminators*
Based on a drift rate of 0.0003%
Droplet |  |  | H2O Droplet | Solids |  | Emissions
Dia. | % mass |  | Mass | Vol. | Dia. | PM | PM10 | PM2.5
(micron) | smaller |  | (g) | (cc) | (micron) | (lb/hr) | (lb/hr) | (lb/hr)
10 | 0 |  | 5.236e-10 | 1.4661e-12 | 1.4095
20 | 0.196 |  | 4.1888e-09 | 1.1729e-11 | 2.8189 |  |  | 0.196%
30 | 0.226 |  | 1.4137e-08 | 3.9584e-11 | 4.2284
40 | 0.514 |  | 3.351e-08 | 9.3829e-11 | 5.6378
50 | 1.816 |  | 6.545e-08 | 1.8326e-10 | 7.0473
60 | 5.702 |  | 1.131e-07 | 3.1667e-10 | 8.4568
70 | 21.348 |  | 1.7959e-07 | 5.0286e-10 | 9.8662
90 | 49.812 |  | 3.817e-07 | 1.0688e-09 | 12.6851 |  | 49.81%
110 | 70.509 |  | 6.9691e-07 | 1.9513e-09 | 15.5041
130 | 82.023 |  | 1.1503e-06 | 3.221e-09 | 18.323
150 | 88.012 |  | 1.7671e-06 | 4.948e-09 | 21.1419
180 | 91.032 |  | 3.0536e-06 | 8.5502e-09 | 25.3703
210 | 92.468 |  | 4.849e-06 | 1.3577e-08 | 29.5987
240 | 94.091 |  | 7.2382e-06 | 2.0267e-08 | 33.827
270 | 94.689 |  | 1.0306e-05 | 2.8857e-08 | 38.0554
300 | 96.288 |  | 1.4137e-05 | 3.9584e-08 | 42.2838
350 | 97.011 |  | 2.2449e-05 | 6.2858e-08 | 49.3311
400 | 98.34 |  | 3.351e-05 | 9.3829e-08 | 56.3784
450 | 99.071 |  | 4.7713e-05 | 1.336e-07 | 63.4257 | 99.07%
500 | 99.071 |  | 6.545e-05 | 1.8326e-07 | 70.473
600 | 100 |  | 0.0001131 | 3.1667e-07 | 84.5676
* Reisman, J. and G. Frisbie. 2002. “Calculating Realistic PM10 Emissions from Cooling Towers.”
Environmental Progress & Sustainable Energy. American Institute of Chemical Engineers. Volume 21,
Issue 2, pp. 127-130. July 2002.
** Maximum droplet size governed by atmospheric dispersion. Larger droplets fall to the ground before
evaporating into a particle (EPA 1979).
EXAMPLE CALCULATIONS: |  |  | High Efficiency
Annual drift:
12000 | gal water | 8.33 | lb | 60 | min | 0.0005% | (drift) | = | 29.988 | lb water drift
1 | min | 1 | gal water | 1 | hr |  |  |  |  | hr
Total Particulate Emissions
29.988 | lb water | 7000 | lb PM | 99.07% | PM | = | 0.20797 | lb PM | = | 0.91089 | ton PM
| hr | 1000000 | lb water |  |  |  |  | hr |  |  | yr
PM10 Emissions
29.988 | lb water | 7000 | lb PM | 49.81% | PM10 | = | 0.10456 | lb PM10 | = | 0.45799 | ton PM10
| hr | 1000000 | lb water |  |  |  |  | hr |  |  | yr
PM2.5 Emissions
29.988 | lb water | 7000 | lb PM | 0.196% | PM2.5 | = | 0.00041144 | lb PM2.5 | = | 0.0018021 | ton PM2.5
| hr | 1000000 | lb water |  |  |  |  | hr |  |  | yr